SECTION 075423 - THERMOPLASTIC POLYOLEFIN (TPO) ROOFING

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Adhered TPO membrane roofing system.

          - Roof insulation.

      - PERFORMANCE REQUIREMENTS

        - General Performance:  Installed membrane roofing and base flashings shall withstand specified uplift pressures, thermally induced movement, and exposure to weather without failure due to defective manufacture, fabrication, installation, or other defects in construction.  Membrane roofing and base flashings shall remain watertight.

        - Material Compatibility:  Provide roofing materials that are compatible with one another under conditions of service and application required, as demonstrated by membrane roofing manufacturer based on testing and field experience.

        - Roofing System Design:  Provide membrane roofing system that is identical to systems that have been successfully tested by a qualified testing and inspecting agency to resist uplift pressure calculated according to ASCE/SEI 7.

        - FM Approvals Listing:  Provide membrane roofing, base flashings, and component materials that comply with requirements in FM Approvals 4450 and FM Approvals 4470 as part of a membrane roofing system, and that are listed in FM Approvals' "RoofNav" for Class 1 or noncombustible construction, as applicable.  Identify materials with FM Approvals markings.

          - Fire/Windstorm Classification:  Class 1A-90.

      - SUBMITTALS

        - Product Data:  For each type of product indicated.

        - Shop Drawings:  For roofing system.  Include plans, sections, details, and attachments to other work.

          - Base flashings and membrane terminations.

          - Roof plan showing orientation of membrane.

          - Insulation fastening patterns for corner, perimeter, and field-of-roof locations.

        - Samples for Verification:  For the following products:

          - Sheet roofing, of color specified, including T-shaped side and end lap seam.

          - Roof insulation.

          - Walkway pads.

          - Metal termination bars.

          - Six insulation fasteners of each type, length, and finish.

        - Qualification Data:  For qualified Installer and manufacturer.

        - Manufacturer Certificates:  Signed by roofing manufacturer certifying that roofing system complies with requirements specified in "Performance Requirements" Article.

        - Warranties:  Sample of special warranties.

      - QUALITY ASSURANCE

        - Manufacturer Qualifications:  A qualified manufacturer that is FM approved for membrane roofing system identical to that used for this Project.

        - Installer Qualifications:  A qualified firm that is approved, authorized, or licensed by membrane roofing system manufacturer to install manufacturer's product and that is eligible to receive manufacturer's special warranty.

        - Exterior Fire-Test Exposure:  ASTM E 108,Class A; for application and roof slopes indicated, as determined by testing identical membrane roofing materials by a qualified testing agency.  Materials shall be identified with appropriate markings of applicable testing agency.

      - DELIVERY, STORAGE, AND HANDLING

        - Deliver roofing materials to Project site in original containers with seals unbroken and labeled with manufacturer's name, product brand name and type, date of manufacture, approval or listing agency markings, and directions for storing and mixing with other components.

        - Store liquid materials in their original undamaged containers in a clean, dry, protected location and within the temperature range required by roofing system manufacturer.  Protect stored liquid material from direct sunlight.

          - Discard and legally dispose of liquid material that cannot be applied within its stated shelf life.

        - Protect roof insulation materials from physical damage and from deterioration by sunlight, moisture, soiling, and other sources.  Store in a dry location.  Comply with insulation manufacturer's written instructions for handling, storing, and protecting during installation.

        - Handle and store roofing materials and place equipment in a manner to avoid permanent deflection of deck.

      - PROJECT CONDITIONS

        - Weather Limitations:  Proceed with installation only when existing and forecasted weather conditions permit roofing system to be installed according to manufacturer's written instructions and warranty requirements.

      - WARRANTY

        - Special Warranty:  Manufacturer's standard or customized form, without monetary limitation, in which manufacturer agrees to repair or replace components of membrane roofing system that fail in materials or workmanship within specified warranty period.

          - Special warranty includes membrane roofing, base flashings, roof insulation, fasteners, cover boards, roofing accessories, and other components of membrane roofing system.

          - Warranty Period:  20 years from date of Substantial Completion.

        - Special Project Warranty:  Submit roofing Installer's warranty, on warranty form at end of this Section, signed by Installer, covering the Work of this Section, including all components of membrane roofing system such as membrane roofing, base flashing, roof insulation, fasteners, cover boards, substrate boards, vapor retarders, roof pavers, and walkway products, for the following warranty period:

          - Warranty Period:  Five years from date of Substantial Completion.

- PRODUCTS

      - TPO MEMBRANE ROOFING

        - Fabric-Reinforced Thermoplastic Polyolefin Sheet:  ASTM D 6878, internally fabric or scrim reinforced, uniform, flexible TPO sheet.

          - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

            - Firestone Building Products Company.

            - GAF Materials Corporation.

            - GenFlex Roofing Systems.

            - Johns Manville.

            - Mule-Hide Products Co., Inc.

          - Thickness 60 mils nominal.

          - Exposed Face Color:  White.

      - AUXILIARY MEMBRANE ROOFING MATERIALS

        - General:  Auxiliary membrane roofing materials recommended by roofing system manufacturer for intended use, and compatible with membrane roofing.

          - Liquid-type auxiliary materials shall comply with VOC limits of authorities having jurisdiction.

        - Sheet Flashing:  Manufacturer's standard unreinforced thermoplastic polyolefin sheet flashing, 55 mils thick, minimum, of same color as sheet membrane.

        - Bonding Adhesive:  Manufacturer's standard.

        - Metal Termination Bars:  Manufacturer's standard, predrilled stainless-steel or aluminum bars, approximately 1 by 1/8 inch thick; with anchors.

        - Fasteners:  Factory-coated steel fasteners and metal or plastic plates complying with corrosion-resistance provisions in FM Approvals 4470, designed for fastening membrane to substrate, and acceptable to membrane roofing system manufacturer.

        - Miscellaneous Accessories:  Provide pourable sealers, preformed cone and vent sheet flashings, preformed inside and outside corner sheet flashings, T-joint covers, lap sealants, termination reglets, and other accessories.

      - ROOF INSULATION

        - General:  Preformed roof insulation boards manufactured or approved by TPO membrane roofing manufacturer, selected from manufacturer's standard sizes suitable for application, of thicknesses indicated and that produce FM Approvals-approved roof insulation.

        - Polyisocyanurate Board Insulation:  ASTM C 1289, Type II, Class 1, Grade 2, felt or glass-fiber mat facer on both major surfaces.

        - Provide preformed saddles, crickets, tapered edge strips, and other insulation shapes where indicated for sloping to drain.  Fabricate to slopes indicated.

      - INSULATION ACCESSORIES

        - General:  Furnish roof insulation accessories recommended by insulation manufacturer for intended use and compatibility with membrane roofing.

        - Fasteners:  Factory-coated steel fasteners and metal or plastic plates complying with corrosion-resistance provisions in FM Approvals 4470, designed for fastening roof insulation and cover boards to substrate, and acceptable to roofing system manufacturer.

        - Cover Board:  Fiberboard high density, 1/4 inch thick, R.3.

      - WALKWAYS

        - Flexible Walkways:  Factory-formed, nonporous, heavy-duty, slip-resisting, surface-textured walkway pads or rolls, approximately 3/16 inch thick and acceptable to membrane roofing system manufacturer.

          - Exposed Face Color:  White

- EXECUTION

      - EXAMINATION

        - Examine substrates, areas, and conditions, with Installer present, for compliance with the following requirements and other conditions affecting performance of roofing system:

          - Verify that roof openings and penetrations are in place and curbs are set and braced and that roof drain bodies are securely clamped in place.

          - Verify that wood blocking, curbs, and nailers are securely anchored to roof deck at penetrations and terminations and that nailers match thicknesses of insulation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

        - Clean substrate of dust, debris, moisture, and other substances detrimental to roofing installation according to roofing system manufacturer's written instructions.  Remove sharp projections.

        - Prevent materials from entering and clogging roof drains and conductors and from spilling or migrating onto surfaces of other construction.  Remove roof-drain plugs when no work is taking place or when rain is forecast.

        - Complete terminations and base flashings and provide temporary seals to prevent water from entering completed sections of roofing system at the end of the workday or when rain is forecast.  Remove and discard temporary seals before beginning work on adjoining roofing.

      - INSULATION INSTALLATION

        - Coordinate installing membrane roofing system components so insulation is not exposed to precipitation or left exposed at the end of the workday.

        - Comply with membrane roofing system and insulation manufacturer's written instructions for installing roof insulation.

        - Install insulation under area of roofing to achieve required thickness.  Where overall insulation thickness is 3 inches or greater, install two or more layers with joints of each succeeding layer staggered from joints of previous layer a minimum of 6 inches in each direction.

        - Trim surface of insulation where necessary at roof drains so completed surface is flush and does not restrict flow of water.

        - Install insulation with long joints of insulation in a continuous straight line with end joints staggered between rows, abutting edges and ends between boards.  Fill gaps exceeding 1/4 inch with insulation.

          - Cut and fit insulation within 1/4 inch of nailers, projections, and penetrations.

        - Mechanically Fastened Insulation:  Install each layer of insulation and secure to deck using mechanical fasteners specifically designed and sized for fastening specified board-type roof insulation to deck type.

          - Fasten insulation according to requirements in FM Approvals' "RoofNav" for specified Windstorm Resistance Classification.

          - Fasten insulation to resist uplift pressure at corners, perimeter, and field of roof.

        - Install cover boards over insulation with long joints in continuous straight lines with end joints staggered between rows.  Offset joints of insulation below a minimum of 6 inches in each direction.  Loosely butt cover boards together and adhere to roof insulation.

          - Fasten cover boards according to requirements in FM Approvals' "RoofNav" for specified Windstorm Resistance Classification.

          - Fasten cover boards to resist uplift pressure at corners, perimeter, and field of roof.

      - ADHERED MEMBRANE ROOFING INSTALLATION

        - Adhere membrane roofing over area to receive roofing and install according to membrane roofing system manufacturer's written instructions.

        - Start installation of membrane roofing in presence of membrane roofing system manufacturer's technical personnel.

        - Accurately align membrane roofing and maintain uniform side and end laps of minimum dimensions required by manufacturer.  Stagger end laps.

        - Bonding Adhesive:  Apply to substrate and underside of membrane roofing at rate required by manufacturer and allow to partially dry before installing membrane roofing.  Do not apply to splice area of membrane roofing.

        - In addition to adhering, mechanically fasten membrane roofing securely at terminations, penetrations, and perimeter of roofing.

        - Apply membrane roofing with side laps shingled with slope of roof deck where possible.

        - Seams:  Clean seam areas, overlap membrane roofing, and hot-air weld side and end laps of membrane roofing and sheet flashings according to manufacturer's written instructions to ensure a watertight seam installation.

          - Test lap edges with probe to verify seam weld continuity.  Apply lap sealant to seal cut edges of sheet membrane.

          - Verify field strength of seams a minimum of twice daily and repair seam sample areas.

          - Repair tears, voids, and lapped seams in roofing that does not comply with requirements.

        - Spread sealant bed over deck drain flange at roof drains and securely seal membrane roofing in place with clamping ring.

      - BASE FLASHING INSTALLATION

        - Install sheet flashings and preformed flashing accessories and adhere to substrates according to membrane roofing system manufacturer's written instructions.

        - Apply bonding adhesive to substrate and underside of sheet flashing at required rate and allow to partially dry.  Do not apply to seam area of flashing.

        - Flash penetrations and field-formed inside and outside corners with cured or uncured sheet flashing.

        - Clean seam areas, overlap, and firmly roll sheet flashings into the adhesive.  Hot-air weld side and end laps to ensure a watertight seam installation.

        - Terminate and seal top of sheet flashings.

      - WALKWAY INSTALLATION

        - Flexible Walkways:  Install walkway products in locations indicated.  Heat weld to substrate or adhere walkway products to substrate with compatible adhesive according to roofing system manufacturer's written instructions.

      - FIELD QUALITY CONTROL

        - Final Roof Inspection:  Arrange for roofing system manufacturer's technical personnel to inspect roofing installation on completion.

        - Repair or remove and replace components of membrane roofing system where inspections indicate that they do not comply with specified requirements.

        - Additional inspections, at Contractor's expense, will be performed to determine compliance of replaced or additional work with specified requirements.

      - PROTECTING AND CLEANING

        - Protect membrane roofing system from damage and wear during remainder of construction period.  When remaining construction will not affect or endanger roofing, inspect roofing for deterioration and damage, describing its nature and extent in a written report, with copies to Architect and Owner.

        - Correct deficiencies in or remove membrane roofing system that does not comply with requirements; repair substrates; and repair or reinstall membrane roofing system to a condition free of damage and deterioration at time of Substantial Completion and according to warranty requirements.

      - ROOFING INSTALLER'S WARRANTY

        - WHEREAS <Insert name> of <Insert address>, herein called the "Roofing Installer," has performed roofing and associated work ("work") on the following project:

          - Owner:  <Insert name of Owner>.

          - Address:  <Insert address>.

          - Building Name/Type:  <Insert information>.

          - Address:  <Insert address>.

          - Area of Work:  <Insert information>.

          - Acceptance Date:  <Insert date>.

          - Warranty Period:  <Insert time>.

          - Expiration Date:  <Insert date>.

        - AND WHEREAS Roofing Installer has contracted (either directly with Owner or indirectly as a subcontractor) to warrant said work against leaks and faulty or defective materials and workmanship for designated Warranty Period,

        - NOW THEREFORE Roofing Installer hereby warrants, subject to terms and conditions herein set forth, that during Warranty Period he will, at his own cost and expense, make or cause to be made such repairs to or replacements of said work as are necessary to correct faulty and defective work and as are necessary to maintain said work in a watertight condition.

        - This Warranty is made subject to the following terms and conditions:

          - Specifically excluded from this Warranty are damages to work and other parts of the building, and to building contents, caused by:

            - Lightning;

            - Peak gust wind speed exceeding 72 mph;

            - Fire;

            - Failure of roofing system substrate, including cracking, settlement, excessive deflection, deterioration, and decomposition;

            - Faulty construction of parapet walls, copings, chimneys, skylights, vents, equipment supports, and other edge conditions and penetrations of the work;

            - Vapor condensation on bottom of roofing; and

            - Activity on roofing by others, including construction contractors, maintenance personnel, other persons, and animals, whether authorized or unauthorized by Owner.

          - When work has been damaged by any of foregoing causes, Warranty shall be null and void until such damage has been repaired by Roofing Installer and until cost and expense thereof have been paid by Owner or by another responsible party so designated.

          - Roofing Installer is responsible for damage to work covered by this Warranty but is not liable for consequential damages to building or building contents resulting from leaks or faults or defects of work.

          - During Warranty Period, if Owner allows alteration of work by anyone other than Roofing Installer, including cutting, patching, and maintenance in connection with penetrations, attachment of other work, and positioning of anything on roof, this Warranty shall become null and void on date of said alterations, but only to the extent said alterations affect work covered by this Warranty.  If Owner engages Roofing Installer to perform said alterations, Warranty shall not become null and void unless Roofing Installer, before starting said work, shall have notified Owner in writing, showing reasonable cause for claim, that said alterations would likely damage or deteriorate work, thereby reasonably justifying a limitation or termination of this Warranty.

          - During Warranty Period, if original use of roof is changed and it becomes used for, but was not originally specified for, a promenade, work deck, spray-cooled surface, flooded basin, or other use or service more severe than originally specified, this Warranty shall become null and void on date of said change, but only to the extent said change affects work covered by this Warranty.

          - Owner shall promptly notify Roofing Installer of observed, known, or suspected leaks, defects, or deterioration and shall afford reasonable opportunity for Roofing Installer to inspect work and to examine evidence of such leaks, defects, or deterioration.

          - This Warranty is recognized to be the only warranty of Roofing Installer on said work and shall not operate to restrict or cut off Owner from other remedies and resources lawfully available to Owner in cases of roofing failure.  Specifically, this Warranty shall not operate to relieve Roofing Installer of responsibility for performance of original work according to requirements of the Contract Documents, regardless of whether Contract was a contract directly with Owner or a subcontract with Owner's General Contractor.

        - IN WITNESS THEREOF, this instrument has been duly executed this <Insert day> day of <Insert month>, <Insert year>.

          - Authorized Signature:  <Insert signature>.

          - Name:  <Insert name>.

          - Title:  <Insert title>.

END OF SECTION 075423